A reliable approach for detection of incipient faults of
short-circuits in induction generators using machine
learning
a
a
a
Pedro Pedrosa Rebou¸cas Filho
, Navar M. M. Nascimento
, Igor R. Sousa
,
a
b
Cl´
audio M. S. Medeiros
, Victor Hugo C. de Albuquerque
a
Laborat´orio de Processamento de Imagens, Sinais e Computa¸c˜ao Aplicada, Instituto
Federal
do Cear´a, Fortaleza, CE, Brazil.
b
Programa de P´os-Gradua¸
c˜ao em Inform´atica Aplicada, Universidade de Fortaleza,
Fortaleza, Cear´a, Brazil.
Abstract
This research contributes with a solid approach to detect incipient sta-
tor winding inter-turn short-circuits in induction generators applied in wind
turbines.
A test-bench of
a wind turbine was used and different types of
short-circuit faults are inserted in the generator.
Electrical
current is ac-
quired to build a fault database.
We propose the use of
four feature ex-
traction techniques with three classifiers.
The MLP identified 100% of the
generator’s Normal conditions with less than 1% false positives and negatives.
To classify the fault type,
different topologies of the MLP were used and it
was possible to identify incipient short-circuits in 1.41% turns with 99.33%
accuracy.
The combination Fourier-MLP is more effective for fault detec-
tion, since it obtained 84.48% of accuracy, with 99.98% of Normal conditions
correctly classified.
Keywords:
Fault detection, Induction Generator, Machine learning, Neural
Networks, Reliability, Short-circuit, Wind Turbine.
∗
Corresponding author.
email:
pedrosarf@ifce.edu.br
Email
addresses:
pedrosarf@ifce.edu.br (Pedro Pedrosa Rebou¸
cas Filho),
navarmedeiros@ppger.ifce.edu.br (Navar M. M. Nascimento),
igor.sousa@ppger.ifce.edu.br (Igor R. Sousa), claudiosa@ifce.edu.br (Cl´
audio M.
S. Medeiros), victor.albuquerque@unifor.br (Victor Hugo C. de Albuquerque)
Preprint submitted to Computers & Electrical
Engineering
July 2, 2018

---
1.
Introduction
Among the renewable energy sources, wind energy has become the most
effective and accepted solution for
electricity generation worldwide,
con-
tributing 486.7 GW to global demand [1].
This energy production represents
only 3% of the world’s energy demand,
but it is estimated that in 2030 the
wind power will be able to supply 17-19% of the global demand [1].
Despite the growing exploitation of this energy source at 17% per year [1]
the technologies are not consolidated, there are still engineering and science
challenges to be solved to support this expansion.
Operational
problems directly impact on the cost of
energy,
according
to Polinder,
Ferreira,
Jensen,
Abrahamsen,
Atallah and McMahon [2]
only
with a reliable and available wind turbine system that the cost of energy can
be mitigated.
And in the light of reliability are the maintenance operating
costs, which account for up to 30% of the cost of energy [2].
The concern with maintenance in wind farms has already been evidenced
by Hahn,
Durstewitz and Michael
[3],
in its study the main components of
a wind turbine and the severity for the wind farms are exhibited if there are
stops of the wind turbine for that reason.
The compilation of data from a
set of wind farms installed in Europe has shown that the most costly faulty
component for the wind farm is the electric generator.
Among the areas of study surrounding wind turbines, the present text fo-
cuses on electric generators, especially the Squirrel Cage Induction Generator
(SCIG). The importance of the SCIG is based on its robustness, consolidated
technology and future trends.
And,
Yaramasu,
Wu,
Sen,
Kouro and Nari-
mani [4] forecasts this generator will dominate the market of wind turbine in
the next years.
Despite the versatility of SCIG, it is not immune to faults, and has lim-
itations.
In general
terms,
these faults are associated with:
overheating,
electrical,
dynamic and mechanical
effects [5].
Bonnet and Soukup [5]
em-
phasizes that the short-circuit between turns is the most incipient fault and
the most difficult to detect.
So, this work focus on detecting incipient short-circuits in SCIG, in order
to provide a means to improve wind turbine reliability.
And,
this could be
potentially good for larger wind turbines.
Because,
detecting an incipient
short-circuit before total degradation could guide corrective maintenance to
make repairs on site, without having to remove the generator from the wind
turbine and decrease the machine availability.
2

---
Since wind turbines are a sensor-based equipment,
monitored and con-
trolled by a Supervisory Control
and Data Acquisition (SCADA) system,
the incipient short-circuit detector could be deployed inside the hardware
responsible for data acquisition.
This makes the methodology purposed in
our work feasible to be replicate in real wind turbine systems.
This paper is organized as follows:
in Section 2 a state of the art in fault
detection for reliability improvement in electrical
machines is presented;
in
Section 3 the feature extractions methods used in this work are explained;
in Section 4 the procedures to emulate the fault emulation,
acquire data
and create a dataset for pattern recognition are presented;
in Section 5 the
machine learning methods used in this work are describe, as well its configu-
rations and metrics for evaluations; in Section 6 our results are analyzed and
conclusions presented in Section 7.
2.
State of the art in short-circuit faults in electrical machines
Stator winding faults are usually associated with a variety of
factors,
such as, overheating, electrical overload, electrical discharges and mechanical
stress [5].
This is the environment where the SCIG installed a wind turbine
is operating, so a monitoring tool is required.
The Current Signature Analysis (MCSA) technique was identified as a
promising mean to describe induction generator operational
conditions.
It
consists of a set of consolidated methods, which developed between the years
of 1975 and 1985 in surveys around the world that had in common the analysis
of the current and its spectrum to characterize induction machines [6].
In Morsalin, Mahmud, Mohiuddin, Halim and Saha [7], a neural classifier
is trained with the motor current,
the supply voltage and the rotor speed.
The authors use a single-phase,
0.5 hp motor running at 50 Hz unloaded.
The were considered satisfactory.
However,
the problem is limited to only
one motor configuration (single phase,
no load,
operating at 50 Hz) and
requires a speed sensor along with the already installed current sensors.
Bouzid and Champenois [8]
worked on a computational
model
of
a 1.1
kW induction motor under stator winding failure.
The authors used neu-
ral
networks with current analysis,
and was possible to identify 100% of of
the modeled problems.
But,
the simulating only contemplated the machine
operating under 50 Hz.
In Pal´acios,
Silva,
Goedtel,
Godoy,
Lopes and Proc´
opio [9]
the authors
acquire current signals in a 1 hp motor,
with multiple load conditions and
3

---
varying the percentage of turn under short-circuit (3%, 5% and 10%).
They
achieved results from 75% to 98% of accuracy for binary classifications be-
tween normal or fault conditions.
Oliveira,
Silva and Medeiros [10]
uses a single current sensor,
without
speed sensor and short inter-loop faults from 1.4% in an induction electric
machine and can identify 67% of short conditions using neural networks.
The
authors proposed the use of
the MCSA technique,
combined with Fourier,
from the frequency spectrum theory of
Thomson and Fenger [6].
Vieira,
Cunha,
Medeiros and Silva [11]
continued these studies and was able to
develop an embedded system to detect these failures,
based on the Multi-
layer Perceptron (MLP).
The members,
of
the same research group where this work was devel-
oped,
have experience on detection of
incipient short-circuits in induction
motors.
This
was
consolidated during years
and by theirs
publications:
Oliveira,
Medeiros and Pontes [10],
Coelho,
Barreto,
Medeiros and Santos
[12], Vieira, Cunha, Medeiros and Silva [11].
The literature review exhibited most of the researches were concerned in
identifying failure under certain operation conditions, either by frequency or
load,
and without much description of the fault emulations.
The approach
proposed in our research research was built upon the need to a more gener-
alist method,
wherein an expert system could detect failure under different
operational points.
And also, triggered by the fast expansion of wind farms
in the region of Cear´a, Brazil, this present work address the problem to de-
tect incipient faults in generators, since it is unprecedented for both research
group and region.
3.
Feature extraction methods used for induction machines
The Fourier Transform can be used to express time-domain signals into
a frequency domain.
Oliveira,
Silva and Medeiros [10] investigated the har-
monics in electrical current signal from electrical motor under several inter-
turn short-circuits faults and concluded the most important frequencies are
0.5f
, 1.5f
, 2.5f
, 3.0f
, 5.0f
and 7f
,
wherein f
is the stator’s funda-
n
n
n
n
n
n
n
mental
frequency.
Oliveira,
Medeiros
and Pontes
[10],
Coelho,
Barreto,
Medeiros and Santos [12] and Vieira, Medeiros and Silva [11], Vieira, Cunha,
Medeiros and Silva [11]
also used the same frequencies to purpose different
approaches for fault detection in induction motors.
The studies considered
4

---
the electrical machine operating as motor, but we believe the same frequen-
cies will be representative while the machine works as generator.
Thus, the
values of these frequencies,
normalized by its fundamental,
are going to be
used as features.
The Higher-Order Statistics is a promising technique for describe time
domain signals [13].
The usage of Kurtosis was first proposed by Dwyer [14]
as a statistical
tool
to indicate non-Gaussian components in signals.
This
theory is under the High-Order Statistics basis and described it as the fourth
statistical
moment.
But,
Antoni
[15]
highlights the capacity and efficiency
for characterize non-stationary signals.
The advantage of
HOS for signals
was indicate by Mendel [13], and it relies in the robustness (i.e.
filtering) to
Gaussian noise when using moment higher than second order.
The features
extracted from HOS are going to be skewness and kurtosis,
alongside with
variance and rms values.
The Structural Co-occurrence Matrix consists of a method based on co-
occurrence statistics and is directed to the structural
analysis of
discrete
signals,
admitting existing connections between low-level
structures of
two
discrete signals in n-dimensions [16].
Its main characteristic is to introduce
a prior knowledge about the analyzed signals,
emphasizing the detection of
details.
Its output is a a two-dimensional histogram, wherein SCM provides
the co-occurrences between structures of the input signals [16].
The authors
proposed 6 features to be extracted from any signal and its calculations are
shown in its paper.
Among the feature extraction methods used in this paper,
the SCM is the most recent one and has demonstrated being able to recognize
patterns in details from different signals in different applications [17].
4.
Experimental setup and dataset creation
The wind turbine emulation is based on the configuration described by
Yaramasu,
Wu,
Sen,
Kouro and Narimani
[4],
which consists of
a squirrel
cage induction generator, of the type Full-scale e Full-Variable-Speed, which
means that the electric machine is able to generate electrical energy through-
out the entire speed range.
A test bench based on this wind turbine system
was developed for this work and is shown in Figure 1.
The Drive Machine (DM) emulates the transformation of kinetic energy
from the wind in rotating motion to the shaft of the generator,
in allusion
to the blades of
the wind turbine.
The variable wind speed is emulated
by the frequency converter FC-1 that powers the DM.
FC-2 only feeds the
5

---
generator’s stator.
When the frequency set in FC-1 is larger than in FC-2,
the kinetic energy is converted into electrical
energy,
flowing through the
SCIG to the dc-bus of FC-2.
To perform the experiments we used a 4-pole induction generator,
with
mechanical
power of
1 hp,
electrically connected in delta configuration for
power supply voltage of 220 V , and its rated current is 3 A.
Both generator
and drive machine are powered by a WEG CFW-08 frequency converter.
The DM is mechanically coupled to the generator, and we used an induction
motor with the same characteristics and wiring.
The experiments are conducted by a Short-circuit Test Board in Machines
(SCTBM). There is a electrical circuit, which function is to emulate connec-
tions for the short-circuit between turns of
one coil
stator.
It also has an
acquisition and data sending module to acquire the electrical current of the
electric machine.
Fig.
1.
Wind turbine test bench diagram based on the Full-scale e Full-Variable-Speed
configuration.
6

---
4.1.
Modifications on generator for fault emulation
The inter-turn short-circuit is the most primary fault state in stator wind-
ing [5].
It is mostly neglected,
since it usually does not trigger instruments
or circuit protections, but it might reach phase-to-phase or phase-to-ground
short-circuit, which is usually destructive to the electrical machine [5].
The electrical
machine used to acquire operational
data is the same as
used by Oliveira,
Silva and Medeiros [10]
and Vieira,
Cunha,
Medeiros and
Silva [11].
This machine was properly prepared to enable emulation of stator
winding inter-turn short-circuits.
A diagram of the types of short-circuits are exhibit in Figure 2.
The high
impedance (HI),
Figure 2a,
is parallel
path created for the electric current
to flow.
This condition emulates the most incipient short-circuit,
wherein
the insulation is starting to decay until, reaches the low impedance (LI) case,
Figure 2b.
The LI is a condition prior to total degradation, wherein a amount
of turns are under short-circuits.
This is emulated by removing coils turns
from the circuit,
but keeping them immersed in the electromagnetic field.
In both cases the short-circuit current is limited to its rated value,
through
external resistor, in order to protect our generator during experiments.
This
makes all
of
our emulated faults being incipient,
even the LI short-circuit,
because in a real case scenario the current might exceed the rated value.
There is always a question:
how much time does is take for the inter-
turn short-circuit degrade insulation until
the total
failure?
This has been
addressed for researches in Wang and Butler [18]
Neti
and Wilhelm [19],
Tshiloz,
Mohammed and Feehally [20]
over the years,
and there still
not a
general sense or answer.
But, a common opinion of manufacturers and users
is low voltage machines (≤ 1000 V ) resist for longer periods on short-circuit
than higher voltage machines [21].
The evolution of the incipient short-circuit might take dozens of seconds,
minutes or hours.
This certainly is a function of the amount of turns under
failure.
So,
the methodology purposed in this paper is focused on the first
occurrences of the failure, where there is sufficient time for the expert system
detect before total degradation of the generator.
All short-circuits are applied in just one of the phases during experiments,
in the following amount of total’s stator winding:
1.41%, 4.81% and 9.26%.
Combining intensities and types of short-circuit we arrived at 6 different types
of fault.
In the following text HI might be referred as HI-1,
HI-2 and HI-3,
that means HI with 1.41%,
with 4.81% and with 9.26% of
short circuited
7

---
winding respectively and the same is valid to LI faults.
With this arrange it
is possible to emulate the evolution of short-circuit from its most incipient
stage (LI-1) until a more severe condition for the insulation (HI-3), but also
incipient.
This was based in a study made by Bonnet and Soukup [5].
...
1
4
i
1
i
2
A
(a) High Impedance short-circuit (HI).
...
1
4
i
2
A
i
1
(b) Low Impedance short-circuit (LI).
Fig. 2.
Electrical diagram of the modifications for stator inter-turn short-circuit emulation.
4.2.
Experiments
The experimental setup is shown in Figure 3.
To acquire the signal, from
the three current sensors installed,
it was used a data acquisition system of
National Instruments, composed by the (i) NI-USB6009 module programmed
to read a 10 seconds signal,
sampled at 5 kHz,
with 14-bits resolution and
(ii) a LabView interface running in a microcomputer.
This process resulted
in 1356 acquisitions, being 248 Normal conditions and 1108 fault conditions
among 6 different types of faults.
In all experiments the values of frequency
applied into the generator’s stator (f
) are registered, as well as the voltage
g
in the dc-bus of the frequency converter in the generator side (V
) and power
dc
generated (P ).
The f
ranges from 43.65 to 59.27 Hz,
V
from 210 to 380
g
dc
V .
This might contain intel for the further analyses.
The next step is to apply feature extraction methods in order to retrieve
useful information from the electrical current from phase R of the generator.
4.3.
Dataset creation
To compose our datasets we used three different feature extraction meth-
ods:
one time-domain method (i) the Higher-Order Statistics (HOS) and two
8

---
Fig. 3.
The experimental setup.
A is the frequency converter in wind size, B is the coupled
DM and SCIG,
C is the frequency converter in generator side,
D is the SCTBM,
E are
the NI-USB6009 and F is the microcomputer which runs LabView.
frequency-domain methods (ii) the Fourier Transform and (iii) the Structural
Co-occurrence Matrix (SCM). The features used from each one of the meth-
ods are described in Section 3.
The number of features summarized in Table
1.
Additionally to each one of the methods we purpose using the measure-
ments of V
,
f
and I
as features,
as well.
In HOS one of the features
dc
g
Rrms
is the rms value of the current signal, so in this method the only additional
features are dc-bus and generator frequency.
Table 1
Summary of datasets composed by the feature extraction methods.
Feature
Number
Additional
Total
extraction
of features
features
of features
Fourier
6
V
, f
and I
9
dc
g
Rrms
HOS
4
V
and f
6
dc
g
SCM
6
V
, f
and I
9
dc
g
Rrms
1
All
datasets
have 7 classes,
being 1 Normal
and 6 Faults.
The number
1
Databases are availabe at https://github.com/navarmn/Wind_turbine_failure_prediction.
9

---
of
samples are also the same,
1356,
and they split into classes as follows:
Normal conditions has 248 samples,
Fault HI-1 has 203,
HI-2 has 179,
HI-3
has 183, LI-1 has 177, LI-2 has 208 and LI-3 has 158 samples.
5.
Machine learning methods adopted
With the datasets on our hand the trained classifiers are Multi-layer Per-
ceptron, Support Vector Machines, and Bayesian.
First, preliminary studies
to tune hyperparameters in each model are made, in order to the performance
discussion be conclusive and valid.
The Bayesian classifier is considered a statistical technique, being applied
in the classification of samples according to the probability density function
of each one of these samples belonging to a certain class.
Its learning is super-
vised and is based on Bayes Decision Theory.
Bayesian Classifier distributes
the samples according to the value of
the posterior probability,
calculated
from values of the conditional densities and prior probabilities [22].
The in-
spiration for use this classifiers relies on the assumption that variables are
random and could be modeled by a Gaussian probability density function,
we even consider non-random signals as randomly behavior.
The number of
samples in all
datasets is much higher than its dimensionality,
so we used
the independent estimations of the covariance matrix for each class and, this
gives us a quadratic Bayesian classifier.
The Multi-layer Perceptron is a biologically inspired neural network, which
consist in a sensitive input layer, a processing hidden layer and a output layer,
representing a non-linear mapping in an input vector and an output vector
[23].
Its basic unit, commonly called neurons, are in fact Perceptrons, a non-
linear mathematical
and computational
model
for a neuron,
which are all
interconnected layer by layer though numerical
weights.
The learning pro-
cess occur in a training phase, where weights are adjusted recursively based
on the backpropagation of the error.
Non-linear functions are imposed into
hidden neurons as an mean to solve non-linearly separable problems [23].
The premise for using neural networks is a different than the Bayesian classi-
fiers, it is based on the capability to perform a non-linear mapping between
the input/output pair pattern.
In all databases The MLP was trained using gradient descent algorithm
and the following hyperparameters are defined through a grid search:
number
of hidden neurons varying from 1 to 50;
initial
learning rate from 0.001 to
0.5;
momentum rate from 0.1 to 0.5 and number of
epochs from 100 to
10

---
5000.
It was used one hidden layer and hyperbolic tangent was chosen to be
the activation function of all neurons.
After a preliminary investigation the
number of hidden units of the network were 10 at the database formed by
Fourier, 13 at HOS and 9 at SCM.
Support Vector Machines (SVM) are based on the Statistical
Learning
Theory created by Cortes and Vapnik [24].
This technique has as main
objective to determine classes with boundaries that increase the distance
between them.
Originally, SVM was designed to solve binary problems, how-
ever, this technique becomes complicated when used in multi-class problems
and,
therefore,
approaches such as one-versus-one e one-versus-all
are ex-
amples of variations of this method for this purpose.
The kernel
machines
are versatile,
since it combines statical theory with non-linear projection to
a new feature spaces where classes could be easier classified.
It is a differ-
ent paradigm than Bayesian and MLP classifiers.
The SVM configuration is
found automatically using the polynomial kernel.
The hold-out validation on the datasets were performed,
but since the
number of samples per classes are unbalanced a few precautions were taken
care of.
To compose the training set, the class with fewer samples was used
as reference, and 80% of its samples were used for training.
This number of
samples are rated for other classes.
This arrives in a training set with 882
samples,
being 126 per class (65% of total samples).
This processed should
avoid bias during training.
The test set has 474 samples, unbalanced between
classes.
The metrics used to access performance of
all
classifiers are Accuracy
(Acc),
Specificity (Spe),
Sensitivity (Sen) and F-Score (Fsc).
The average
confusion matrix will
be presented and discussed in order to identify where
the misclassifications occurs.
To determinate the classifier robustness the
False-Positive and Negative rates are going to be analyzed, since they repre-
sent Normal
conditions classified as Fault and Fault conditions classified as
Normal, respectively.
6.
Results and discussions
In this section is discussed the results from all
combinations feature ex-
traction methods versus classifiers,
by its end the better configuration is
shown and the second part concerns different propositions to achieve both
accuracy and robustness of the classifier to identify incipient inter-turn stator
winding short-circuit.
11

---
All
results presented are from the test set.
The results on training set
are not exhibited, since they are very similar on test set.
The programming
routines of feature exctaction, trainings and classifications are implemented
on MATLAB
.
Note that all
experiments reported here used a PC Intel
R
i7 running at 3.1 GHz and 8 Gb of
RAM on a Linux Ubuntu operational
system installed in a solid state drive.
6.1.
Comparison of feature extraction methods and classifiers
In Table 2 it is exhibit the average metrics overall classes from all combi-
nations feature extraction method versus classifiers.
Using Fourier as a fea-
ture extractor, MLP achieved average accuracy of 84.48% among all classes,
which is better than Bayes and slightly than SVM. The sensitivity indicates
MLP was far better than other methods while detecting true positive hits,
which might indicate a capability to identify Normal operational conditions
of the generator.
The specificity also indicates MLP better than the other
classifiers while doing predictions of faulty conditions.
The results in Table 2 indicates that combining HOS with SVM provide
better results than MLP and Bayes,
because achieved 89.6% of accuracy in
all classes.
However, the sensibility and specificity of MLP still higher than
Bayes and SVM,
this indicates MLP remain better while detecting Normal
conditions among other classes.
The dataset composed using SCM has shown
results below 50% in MLP,
which is no better than a random prediction.
The same for Bayes,
which is slightly better.
Both methods might be note
suitable for SCM extractor.
But,
SVM provided results much better than
both, achieving 89.14% of accuracy.
The analysis indicates MLP alongside Fourier might be a more robust
approach to detect stator winding inter-turn short-circuits in SCIG, because
its results are more stable than other methods as well its false positive and
negative rates.
But,
in order to affirm this,
the results exhibited in Table 3
and the confusion matrix shown in Table 4 are analyzed.
The highlight on non-fault detection goes to the combination MLP-Fourier
and Bayes-Fourier,
which achieved 99.8% and 99.14% respectively.
Despite
the better overall accuracy of the combination SVM-HOS the Normal condi-
tions were identified, with only 81.17% and it is not suitable for the purpose
of this work, which is to identify faulty conditions it is important the classifier
identify properly Normal operational conditions of the generator.
The most critical fault, LI-3 is properly identified by MLP-Fourier in all
training.
The other faults are correctly classified in the decreasing order:
LI-
12

---
Table 2
Results from average metrics of overall classes:
Accuracy (Acc), Sensitivity (Sen), Speci-
ficity (Spc),
F-score (Fsc) obtained from a extractors Fourier,
HOS and SCM,
combined
with classifiers MLP, SVM and Bayes.
Classifier
Acc (%)
Sen (%)
Spc (%)
Fsc (%)
Fourier
MLP
84.48±2.65
84.48±2.65
97.01±0.59
84.48±2.65
SVM
83.94±1.06
51.31±3.58
91.42±0.59
55.04±2.57
Bayes
77.30±0.63
77.47±1.13
95.33±0.16
77.39±0.81
HOS
MLP
83.54±1.42
83.54±2.31
96.82±0.34
83.54±1.57
SVM
89.60±0.52
76.79±1.35
95.43±0.34
77.08±1.24
Bayes
78.96±0.64
78.96±0.64
95.75±0.16
78.96±0.64
SCM
MLP
40.93±5.58
40.93±7.97
80.61±3.56
40.93±4.75
SVM
89.14±0.74
64.53±2.52
93.13±0.53
62.87±3.32
Bayes
54.97±1.00
55.03±1.05
88.00±0.41
55.03±1.00
2, HI-3, HI-1, HI-2 and LI-1.
In the confusion matrix, Table 4, is is possible
to see fault HI-1 is mostly misclassified as LI-1,
because the low amount of
turns in stator winding under short-circuit, 1.41%, is not enough to provide
significant differences in the current spectra between high and low impedance
types of fault.
The robustness come with the 1% of samples classified as nor-
mal conditions, since the faulty HI-1 tend to be similar to normal operational
condition.
Despite the labeling of high and low impedance short-circuits, all
Faulty classes are incipient, as explained in Section 4.1, so a real-case scenario
is going to be easily detected.
Similar patterns occurs in other groups of faults, HI-2 is mostly confused
with LI-1,
HI-1 and LI-3.
LI-1 misclassified as HI-1,
HI-2,
HI-3,
LI-2 and
LI-3.
But,
faults HI-3,
LI-2 and LI-3 have a higher accuracy rate,
because
the amount of turns under short-circuit grows alongside its discrepancy from
normal conditions and other classes.
Only 4% of the samples in faulty condi-
tions were misclassified as normal,
which indicates the misclassifications by
MLP tend to be between faulty classes and not with normal conditions.
Regarding time analysis our results indicated Fourier took 2.48 ms to
13

---
Table 3
Results of
a average accuracy rate comparison between different generator operational
states (Classes), over the features extraction methods Fourier, HOS and SCM.
Fourier
Class
MLP
SVM
Bayes
Normal
99.98±0.11
80.87±2.27
99.14±0.33
HI-1
73.51±12.26
76.34±1.82
62.94±3.27
HI-2
66.00±8.74
80.26±0.75
54.11±3.28
HI-3
94.05±3.82
81.18±1.88
86.71±1.31
LI-1
58.94±12.36
83.36±2.99
39.49±5.91
LI-2
98.89±1.12
87.66±1.29
92.10±1.21
LI-3
100.00±0.00
97.96±0.17
100.00±0.00
HOS
Class
MLP
SVM
Bayes
Normal
63.93±1.24
81.17±3.30
59.24±4.49
HI-1
74.03±2.60
72.04±0.93
47.46±5.40
HI-2
98.11±1.39
78.10±0.90
96.24±0.77
HI-3
98.25±1.22
88.71±0.27
99.22±0.52
LI-1
80.39±1.71
84.16±1.03
63.23±2.54
LI-2
98.78±0.55
98.20±0.47
100.00±0.00
LI-3
96.88±0.33
99.20±0.53
97.37±0.67
SCM
Class
MLP
SVM
Bayes
Normal
51.59±0.57
77.66±2.12
49.03±3.97
HI-1
31.75±1.70
81.31±1.92
73.51±3.68
HI-2
50.00±0.80
92.63±1.55
10.38±.29
HI-3
46.03±1.09
97.30±0.63
50.12±2.10
LI-1
69.84±2.01
83.14±2.68
17.03±7.14
LI-2
64.29±0.95
97.66±0.96
90.35±1.20
LI-3
90.48±0.44
99.34±0.35
92.87±1.06
extract feature from the current signal
and MLP takes an average of 0.034
ms to classify one sample.
Both feature extraction time and classification
time are around 2.5 ms, and it can be unconsidered for our system, since most
of
the time is spent to acquire the electrical
current.
For our experiments
we used as standard 10 seconds acquisition at 5 kHz to guarantee a 0.1
14

---
Table 4
Percentage average confusion matrix for Fourier-MLP.
The highlights correspond to
correct classifications and are also the accuracy rate of each class, while the other number
are the misclassifications rates.
The sum in each row correspond to 100%.
Predictions
Labels
Normal
HI-1
HI-2
HI-3
LI-1
LI-2
LI-3
Normal
99.98%
0.00%
0.01%
0.00%
0.00%
0.00%
0.00%
HI-1
0.93%
73.50% 4.41%
0.49%
19.25%
0.85%
0.53%
HI-2
1.84%
7.44%
66%
6.38%
14.12%
3.25%
0.95%
HI-3
0.12%
0.82%
3.26% 94.04%
1.00%
0.68%
0.04%
LI-1
1.09%
28.11%
8.84%
1.26%
58.93%
1.04%
0.69%
LI-2
0.02%
0.05%
0.25%
0.49%
0.14%
98.88% 0.15%
LI-3
0.00%
0.00%
0.00%
0.00%
0.00%
0.00%
100%
Hz/sample of resolution in the frequency spectrum.
The total time for our
system to analyze one sample ie 10.0025 seconds.
The research conducted here is investigatory,
in embedded applications
hardware and software optimizations are required,
as a trade-off with accu-
racy.
But, Thomson and Fenger [25] affirms using MCSA we are capable of
detecting incipient short-circuits.
Thomson and Fenger [25]
also performed
several tests of short-circuits on the induction machine operating under rated
voltage.
And,
their results exhibit the lead time until
failure is an order of
minutes, since in our approach took 10.002 seconds to classify on sample, this
is enough time for the expert system detect the failure within time before
total degradation.
We believed the classifier robustness relies not only on its accuracy,
but
in its capability of
identify and reject samples that provide confusion,
like
False-Positives and False-Negative.
Thus,
in order to increase the classifier
reliability, by reducing the amount of faulty conditions misclassified as nor-
mal, it is necessary to induce the classifier to learn differences between faulty
and normal
patterns.
And those results imply faults should be better clas-
sified in groups, so the following experiments are performed by training the
MLP with faults grouped by its type or/and intensity,
since this classifier
obtained the best results.
6.2.
Classifier reliability improvement
In Table 5 the average accuracy of three-class training is shown:
normal
motor,
high impedance fault and low impedance fault.
In this experiment,
15

---
the HI and LI classes do not have all the data, since it would unbalance the
data set in relation to the normal
class.
The Fourier-MLP combination is
also used as the feature extraction-classifier approach.
The MLP achieved
95.15% overall set-up.
It is interesting to note that the Normal class obtained
100% hit rate, there being no False-Positives.
As the confusion matrix shows,
the LI class is confused 11.5% of times with the class HI.
One explanation
is that HI class mix data from HI-1,
HI-2 and HI-3 and as seen in Table 4
HI-1 and LI-1 are highly confused.
And the fact of the short-circuit current is
limited at the generator nominal current in order not to damage the machine,
making the emulated LI short-circuits not much different from HI faults.
Table 5
Summary of
results after grouping faults by two types,
HI and LI.
It is exhibited the
overall
accuracy among all
classes,
as well
its independent rates.
The confusion table is
also shown.
Overall classes
Acc (%)
95.15±0.94
Stratified by classes
Class
Acc (%)
Normal
100±0.00
HI
96.73±2.71
LI
88.71±2.74
Confusion table
Predictions
Labels
Normal
HI
LI
Normal
100%
0%
0%
HI
0.03%
96.73%
3.23%
LI
0.13%
11.15%
88.71%
New trainings are performed, this time between the Normal classes, short-
circuit in 1.41% of
turns (LVL-1),
in 4.81% (LVL-2) and in 9.26 % (LVL-
3).
The result is shown in the Table 6,
where the average accuracy and
the confusion matrix are shown.
Again,
there is suppressed data to avoid
unbalance of
data relative to the Normal
class,
as in the case of
the class
of
levels 1,
2 and 3.
The overall
accuracy increased to 97.12% and it is
notable that once again, the Normal class is classified correctly 100% of the
time.
It is induced to presume the MLP accuracy rate increase following the
16

---
amount of
turns under short-circuit,
because critical
failures tend to show
significantly differences in the current spectra.
But the results indicate a
different behavior by the classifier.
Since the concerning of this works is to
detect incipient faults and the LVL-1 group of
short-circuits are our goal
to identify properly.
They are the most difficult faults to identify,
because
a low amount of
turns are under fault.
However,
the MLP classified them
correctly 99.3% of
the times.
This is a huge improvement since in 7 class
classification,
the faults HI-1 and LI-1 had lower hit rates of
73.50% and
58.93% respectively, as seen in Table 4.
Table 6
Summary of
results after grouping faults by intensities,
1.41%,
4.81% and 9.26%.
It
is exhibited the overall
accuracy among all
classes,
as well
its independent rates.
The
confusion table is also shown.
Overall classes
Acc (%)
97.12±0.97
Stratified by classes
Class
Acc (%)
Normal
100±0.00
LVL-1
99.33±0.70
LVL-2
91.22±3.77
LVL-3
97.92±1.43
Confusion table
Predictions
Labels
Normal
LVL-1
LVL-2
LVL-3
Normal
100%
0%
0%
0%
LVL-1
0.11%
99.33%
0.48%
0.07%
LVL-2
1.56%
4.49%
91.22%
2.71%
LVL-3
0.06%
0.18%
1.83%
97.91%
The LVL-3 achieved high hit rates,
around 97%,
but the intermediary
condition LVL-2 presented the lower hit rate of
all
classes,
only 91.22% in
average.
By the confusion table it is possible to see 4.49% of the LVL-2 faults
were classified as LVL-1,
that occurs because HI-2 faults tend to be similar
to LI-1 and HI-1, as seen in Table 4.
Some of samples are classified as LVL-3,
specially by the confusion between LI-2 and HI-3 and a few less are classified
as Normal.
17

---
A final training is performed with the intention of a binary classification
only the data between Normal and Faults.
For this training, 80% of data were
used for training.
Although classes are unbalanced in number of samples (887
Failure samples and 199 Normal samples), this helps the network learn more
about fault data,
where most of
the knowledge of
the data bank is found.
Thus,
one can avoid cases of False-Positives.
The result is displayed in the
Table 7.
With 100% average accuracy, there is no presence of False-Positive
or False-Negative.
This result was expected,
since the Tabs.
4 to 6 already
indicate values similar to the average accuracy of the Normal class.
In Figure 4,
the output y
(t) of
the best MLP trained with the binary
o
data set on the dataset is presented.
It is possible to observe that although
100% accuracy has been obtained,
some samples tend to be misclassified,
such as the samples marked in the graphs.
To avoid some samples could
possibly be misclassified, we chose to introduce a rejection band at the output
of
the MLP.
If
any sample is within this range,
the sample is rejected by
the network and a new sample is analyzed.
This procedure reduces False-
Positive and False-Negative.
In the specific case of this work, an asymmetric
rejection range between +0.2 and −0.4 was implemented in order to highlight
the decrease of False-Positives,
since erroneous classification of the Normal
condition as a Fault can lead to loss of classifier’s reliability, since the machine
should be stopped for later evaluation.
Table 7
Summary of results, containing accuracy after grouping all faults in one class.
It is exhib-
ited the overall
accuracy among all
classes,
as well
its independent rates.
The confusion
table is also shown.
Overall classes
Acc (%)
100±0.00
Stratified by classes
Class
Acc (%)
Normal
100±0.00
Fault
100±0.00
Confusion table
Predictions
Labels
Normal
Fault
Normal
100%
0%
Fault
0%
100%
18

---
0.98
0.8
0.6
57 06
.
Hz
59.55Hz
54.53Hz
1
210 V
210 V
210 V
0.4
1.1916
A
1.1843
A
1.1731
A
0.2
Rejection
0
threshold
-0.2
-0.4
46.91Hz
44.37Hz
44.47Hz
-0.6
259 V
251 V
210 V
1.5081
A
1.5139
A
A
1.1840
-0.8
-0.98
0
100
200
300
400
500
600
700
800
900
1000
Amostras (t)
Samples (t)
Fig. 4.
Output from the MLP-Fourier fitted under the the binary dataset.
Normal condi-
tions are blue and Fault conditions are red.
The analysis of
the dataset in Figure 4 indicates samples from normal
conditions that are closer to the threshold have a low voltage on the dc-bus,
around 210 V .
This occurs in different generator frequencies and in the faulty
conditions as well.
This might occur because the imbalance produced by the short-circuit
deprecate the generation capability.
This hypothesis is affirmed by the mea-
sured power and dc-bus voltage on the modified generator during the emu-
lations in test-bench.
The sample highlighted by the number 1 in Figures 4,
5a and 5b are the same.
When f
was 59.55 Hz, this was much close to the
g
starting point of the generation curve, this moment might be interpreted as
a low wind-speed condition, as well.
When the generation power capability,
Figure 5b,
is too much under its nominal
rate,
so the V
in the frequency
dc
converter tend to be much less than is rated value.
This might lead to a
misclassification.
This phenomenon incites the usage of a relative frequency
between stator’s and rotor’s generator should me more appropriate to avoid
misclassifications,
but this requires a speed sensor coupled to the genera-
tor.
However, we emphasize the reliability of the classifiers is kept since the
rejection band prevent False-Positive misclassifications.
So,
the comparison and propositions for the classifiers make possible to
19
y
o
(t)

---
identify incipient short-circuits with a reliable classification, in order to meet
necessities of wind farm maintenance routines.
This classifier could prevent
not also unwanted stops of
the wind turbine,
but provide alerts to direct
repair in loco without having to remove generator from site.
This might
potentially reducing downtime in wind farms.
59.27 Hz
59.55Hz
210 V
210 V
1.5609 A
1.1843
A
1
(a)
59.27 Hz
59.55Hz
210 V
210 V
1.5609 A
1.1843
A
1
(b)
Fig. 5.
Curves dc-bus voltage in 5a and power in 5b.
20
V
dc
 (V)

---
6.3.
Comparison to works related
In Pal´acios,
Silva,
Goedtel,
Godoy,
Lopes and Proc´
opio [9]
the authors
trained a MLP and were able to correctly identify 98.96% of the conditions
using 30 features and 85.63% with 7 features reduced with PCA.
While we
achieved 100% with 9 features, as exhibited in Table 7.
Despite varying the
amount of turn under short-circuit the author considered all faulty samples
as faults and as we shown, the main difficult while detecting incipient short-
circuits are the confusion between levels of
short-circuits.
We were able
to identify 1.41% of turn under short-circuit with 99.93% of accuracy with
less than 2% of
false negatives and 0% of
false positives.
Pal´acios,
Silva,
Goedtel, Godoy, Lopes and Proc´opio [9] also acquires its signals with 25 kHz
during 15 seconds,
which might compromise memory storage in embedded
applications, while we did 5 kHz in 10 seconds.
However, the time analysis
was not contemplated by their research.
We exhibited the fault detection is frequency dependent, specially in re-
gions with lower voltage in dc-bus.
So our methodology demonstrated to be
more generalist, instead of they results of In Morsalin, Mahmud, Mohiuddin,
Halim and Saha [7] and Bouzid and Champenois [8], which uses the electrical
machine running at only on frequency.
However, the studies made by previous works in our researches groups, as
Oliveira, Silva and Medeiros [10], Coelho, Barreto, Medeiros and Santos [12]
and Vieira,
Cunha,
Medeiros and Silva [11],
concluded one current sensor
might be suitable to identify short-circuits in induction motors powered by
frequency converters.
Coelho,
Barreto,
Medeiros and Santos [12]
achieved
better results,
and achieved 97.5% of accuracy for binary classifications.
In
fact this is also relevant to our approach,
because using only one current
sensor we obtained around 85% of accuracy rate overall classes and 100% in
binary classifications.
7.
Conclusions
The results from combinations of feature extraction method and classifier
indicated that the combination Foufier and MLP is a better tool to detect in-
cipient stator winding inter-turn short-circuits in induction generator applied
to wind turbines.
It was perceived in all training Normal conditions were classified with hit
rate over 99%, thus by grouping all faults together it was achieved 100% in a
21

---
binary classifications.
Rejection thresholds are implemented to reduce false
positive and negative rates, despite there were none of samples rejected.
Analyzing the outputs from the binary neural
networks it was possible
to identify when dc-bus is far from its rated value (311 V ), Normal samples
tend to be misclassified as faulty, but the classifier reliability is kept by the
rejection band, in order to avoid False-Positives misclassifications.
However, to identify incipient faults it was perceived that grouping faults
in different kind of
groups led to different interpretations.
Therefore,
to
provide an incipient fault detection system a multi-classifier structure,
con-
taining the four, three and two classes MLPs should be used.
It is important
to emphasize all short-circuit conditions evaluated are in fact incipient con-
ditions, since the electrical current value is limited by its rated value.
Thus,
we believe real short-circuit conditions should be easily identified due to our
classifier robustness.
The methodology used in this work demonstrated to be efficient and could
be replicated in SCADA systems that are already installed in wind farms,
and in newer wind turbine as well.
Since recent generators are powered by
frequency converters this solution could also be embedded on it,
creating a
integrated product responsible for powering,
control
and monitoring.
This
certainly would increase reliability and availability of the wind farm.
References
[1]
GWEC.
Global Wind Report 2016.
page 76, 2017.
[2]
Henk Polinder, Jan Abraham Ferreira, Bogi Bech Jensen, Asger B Abrahamsen, Kais
Atallah,
and Richard a.
McMahon.
Trends in Wind Turbine Generator Systems.
IEEE Journal
of Emerging and Selected Topics in Power Electronics,
1(3):174–185,
2013.
[3]
Berthold Hahn, Michael Durstewitz, and Kurt Rohrig.
Reliability of Wind Turbines.
Wind Energy, pages 1–4, 2007.
[4]
Venkata Yaramasu,
Bin Wu,
Paresh C.
Sen,
Samir Kouro,
and Mehdi
Narimani.
High-Power Wind Energy Conversion Systems:
State-of-the-Art and Emerging Tech-
nologies.
Proceedings of the IEEE, 103(5), 2015.
[5]
A. H. Bonnett and G. C. Soukup. Cause and analysis of stator and rotor failures in 3-
phase squirrel cage induction motors. Pulp and Paper Industry Technical Conference,
1991., Conference Record of 1991 Annual, pages 22 – 42, 1991.
22

---
[6]
William T Thomson.
Motor Current Signature Analysis for Incution Motors.
Indus-
trial
Application and Case Histories, pages 359–373, 2017.
[7]
Sayidul
Morsalin,
Khizir Mahmud,
Humaira Mohiuddin,
Md.
Reduanul
Halim,
and
Prattay Saha.
Induction motor inter-turn fault detection using heuristic noninvasive
approach by artificial
neural
network with Levenberg Marquardt algorithm.
IEEE
International
Conference on Informatics, Electronics & Vision (ICIEV), pages 1–6,
2014.
[8]
Monia Ben Khader Bouzid and G´erard Champenois.
Neural network based method
for the automatic detection of the stator faults of the induction motor.
In Electrical
Engineering and Software Applications (ICEESA), 2013 International Conference on,
pages 1–7. IEEE, 2013.
[9]
Rodrigo H Cunha Pal´acios,
Ivan Nunes Silva,
Alessandro Goedtel,
Wagner Fontes
Godoy, Tiago Drummond Lopes, and Corn´elio Proc´opio.
Reconhecedor neural de de-
feitos no estator em motores de indu¸
c˜
ao trifasico apoiado por analise das componentes
principais.
[10]
Atila Gir˜ao Oliveira,
Ricardo Silva,
and Claudio Marques de S´a Medeiros.
Neural
network used to stator winding interturn short-circuit fault detection in an induction
motor driven by frequency converter.
Proceedings - 1st BRICS Countries Congress
on Computational
Intelligence, BRICS-CCI 2013, pages 459–464, 2013.
[11]
Renan Gir˜ao Vieira,
Rebeca G.
C.
Cunha,
Cla´
udio Marques de S´a Medeiros,
and
Elias R.
Silva JR.
Embedding a neural
classifier to detect faults in a three-phase
induction motor.
2016 VI Brazilian Symposium on Computing Systems Engineering
Embedding, 2016.
[12]
David N Coelho, G A Barreto, Cl´audio M S Medeiros, and Jos´e Daniel Alencar Santos.
Performance comparison of classifiers in the detection of short circuit incipient fault
in a three-phase induction motor.
In Computational
Intelligence for Engineering
Solutions (CIES), 2014 IEEE Symposium on, pages 42–48. IEEE, 2014.
[13]
J M Mendel.
Tutorial
on higher-order statistics (spectra) in signal
processing and
system theory:
theoretical
results and some applications.
Proceedings of
the IEEE,
79(3):278–305, 1991.
[14]
R. Dwyer.
Detection of non-Gaussian signals by frequency domain Kurtosis estima-
tion.
ICASSP ’83. IEEE International
Conference on Acoustics, Speech, and Signal
Processing, 8:607–610, 1983.
[15]
J´erˆ
ome Antoni. The spectral kurtosis:
A useful tool for characterising non-stationary
signals.
Mechanical
Systems and Signal
Processing, 20(2):282–307, 2006.
[16]
Geraldo L Bezerra Ramalho, Daniel S Ferreira, Pedro P Rebou¸cas Filho, and F´atima
N Sombra de Medeiros.
Rotation-invariant feature extraction using a structural co-
occurrence matrix.
Measurement, 94:406–415, 2016.
23

---
[17]
Pedro P Rebou¸
cas Filho,
Elizˆangela de S Rebou¸cas,
Leandro B Marinho,
R´
oger M
Sarmento,
Jo˜ao Manuel
RS Tavares,
and Victor Hugo C de Albuquerque.
Analysis
of human tissue densities:
A new approach to extract features from medical images.
Pattern Recognition Letters, 94:211–218, 2017.
[18]
Hang Wang and Karen L Butler. Modeling transformers with internal incipient faults.
IEEE Transactions on power delivery, 17(2):500–509, 2002.
[19]
Prabhakar Neti
and Brant Wilhelm.
Online health monitoring of motor insulation.
General
Electric Company, 2013.
[20]
K Tshiloz, AC Smith, A Mohammed, S Djurovi´c, and T Feehally. Real-time insulation
lifetime monitoring for motor windings.
In Electrical
Machines (ICEM), 2016 XXII
International
Conference on, pages 2335–2340. IEEE, 2016.
[21]
William T Thomson.
On-line mcsa to diagnose shorted turns in low voltage stator
windings of 3-phase induction motors prior to failure. In Electric Machines and Drives
Conference, 2001. IEMDC 2001. IEEE International, pages 891–898. IEEE, 2001.
[22]
Murillo B Rodrigues,
Raul
Victor M Da N´obrega,
Shara Shami
A Alves,
Pedro Pe-
drosa Rebou¸cas Filho, Jo˜
ao Batista F Duarte, Arun K Sangaiah, and Victor Hugo C
De Albuquerque.
Health of
things algorithms for malignancy level
classification of
lung nodules.
IEEE Access, 6:18592–18601, 2018.
[23]
Pedro Pedrosa Rebou¸
cas Filho, Paulo C´esar Cortez, Antˆ
onio C da Silva Barros, Victor
Hugo C Albuquerque, and Jo˜
ao Manuel RS Tavares.
Novel and powerful 3d adaptive
crisp active contour method applied in the segmentation of ct lung images.
Medical
image analysis, 35:503–516, 2017.
[24]
Edson Cavalcanti Neto, Samuel Luz Gomes, Pedro Pedrosa Rebou¸
cas Filho, and Vic-
tor Hugo C. de Albuquerque.
Brazilian vehicle identification using a new embedded
plate recognition system.
Measurement, 70:36 – 46, 2015.
[25]
William T. Thomson and Mark Fenger. Current signature analysis to detect induction
motor faults.
IEEE Industry Applications Magazine, 7(4):26–34, 2001.
24

---
Pedro Pedrosa Rebou¸cas Filho - PhD degree in Teleinformatics En-
gineering from Federal University of Cear´
a, Brazil, in 2013, and is a professor
at Federal Institute of Education, Science and Technology of Cear´a (IFCE),
Brazil.
His current researches interest are applications in Computer Vision.
For more information:
https://professorpedrosa.com/
Navar de Medeiros Mendon¸ca e Nascimento - Master of Science in
Renewable Energies from Federal Institute of Education, Science and Tech-
nology of
Cear´
a (IFCE) in 2018.
Received the Bachelor degree in Mecha-
tronics Engineering from Institute of Education,
Science and Technology of
Cear´
a,
Brazil,
in 2015.
His current researches interest are applications in
Pattern Recognition,
Computer Vision,
Electrical
Machines and Renewable
energies.
Igor Rocha de Sousa - Master degree student in Renewable Energies
at Federal Institute of Education, Science and Technology of Cear´a (IFCE),
received the Bachelor degree in Mechatronics Engineering from Institute of
Education,
Science and Technology of
Cear´
a (IFCE),
Brazil,
in 2017.
His
current researches interest are applications in Pattern Recognition, Computer
Vision and Electrical Machines and Renewable energies.
Cl´audio Marques de S´a Medeiros - PhD degree in Teleinformatics
Engineering from Federal
University of
Cear´
a,
Fortaleza,
/Brazil,
in 2008,
and is a professor at Federal
Institute of
Education,
Science and Technol-
ogy of
Cear´a (IFCE),
Fortaleza,
Brazil.
His current researches interest is
applications in Machine Learning, Electrical Machine Failure Detection and
Renewable Energies.
Victor Hugo C.
de Albuquerque - PhD in Mechanical
Engineering
with emphasis on Materials from the Federal University of Paraiba (UFPB,
2010), an MSc in Teleinformatics Engineering from the Federal University of
Ceara (UFC, 2007).
He is currently Assistant VI Professor of the Graduate
Program in Applied Informatics at the University of Fortaleza (UNIFOR).
25